## Sheet1
AVR Selection Chart and Failure Report
※Please send file to Kutai or your local service provider when completed
All fields marked with a red asterisk (*) are required, please check before submitting.
|  | Customer: | [15 empty] | Filled by: | [16 empty] | Date:
* | 1 | Kutai AVR model: | [11 empty] | Serial: | [16 empty] | Purchase date:
* | 2 | Generator brand: | [11 empty] | Model: | [14 empty] | Original AVR model:
| 3 | Generator rated capacity: | [13 empty] | KVA | [10 empty] | KW | [7 empty] | VAC | Hz
| 4 | Operation type: |  |  | Single operation | [9 empty] | Paralleled operation
| 5 | Load type: |  | Mixed (Multiple) | [6 empty] | Resistive | [7 empty] | Capacitive | [6 empty] | No linearity | [5 empty] | Other
| 6 | Phase: | Single Phase 2 wire | [8 empty] | Single Phase 3 wire | [12 empty] | 3 Phase 3 wire | [7 empty] | 3 Phase 4 wire
| 7 | Working frequency: |  |  |  |  | 50HZ |  |  |  | 60HZ
* | 8 | Excitation: |  | Brush type |  |  |  |  | Brushless type
* | 9 | Excitation Source: |  |  |  | Self excited | [6 empty] | Permanent generator (PMG) | [14 empty] | Harmonic winding (Compound winding)
* | 10 | Excitation resistance: | [11 empty] | ohm
| 11 | Excitation winding insulation resistance: | [21 empty] | ohm
| 12 | Stator coil insulation resistance: | [17 empty] | ohm
* | 13 | Without load excitation voltage: | [17 empty] | VDC
| 14 | Maximum excitation voltage: | [15 empty] | VDC
* | 15 | Maximum excitation current: | [15 empty] | ADC
| 16 | Residual voltage: | [8 empty] | VAC
* | 17 | AVR sensing input voltage: | [14 empty] | VAC
* | 18 | AVR power input voltage: | [14 empty] | VAC
| 19 | Time required to reach rate RPM: | [18 empty] | sec.
| 20 | External voltage potentiometer used: | [11 empty] | Yes |  |  |  |  | NO |  |  |  | Open connection | [6 empty] | Close connections
* | 21 | AVR failure description: | [5 empty] | No voltage | [6 empty] | Unstable | [6 empty] | Over voltage | [6 empty] | Voltage decrease or increase (Oscillation)
| 22 | AVR appearance: |  |  | Visible burn sign | [8 empty] | No visible burn sign
| 23 | Generator produce no voltage: | [7 empty] | At starts | [6 empty] | When adding load | [9 empty] | After applying load for a period of time
| 24 | Condition of the fuse on the AVR: | [9 empty] | Burnt | [5 empty] | Good
| 25 | Generator externally excited and tested with a 12Volt battery: | [22 empty] | Yes |  |  | No
| 26 | Voltage output of generator when excited with 12Volt battery: | [27 empty] | VAC
| 27 | Generator voltage without load: | [7 empty] | Stable | [6 empty] | Unstable
| 28 | Generator voltage with load: | [6 empty] | Stable | [5 empty] | Unstable | [6 empty] | Over increase or decrease | [11 empty] | Overtime on recovering
| 29 | Engine rotating speed: | [5 empty] | Stable |  |  |  |  | Unstable
| 30 | Is this a military generator with manual backup excitation: | [21 empty] | Yes |  |  | No
Usage Description or Comments
Please send the completed Survey to kutai2017@kutai.com.tw
Or Mail to Kutai Electronics Co., LTD
3, Lane 201, Chien Fu St., Chyan Jenn Dist.,
Kaohsiung, Taiwan
http://www.kutai.com.tw